## Slide 1: Rad na projektnom zadatku Proračun vremena evakuacije
dr Emina Mihajlović, red. prof.
Nikola Mišić, asistent
OAS – Zaštita na radu
Predmet: Sredstva i oprema za gašenje požara
05.04.2023.

## Slide 4: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Prema SRPS TP 21 iz 2003. godine prosečna brzina kretanja čoveka po ravnoj podlozi na otvorenom prostoru je:
  1,5 m/s, odnosno 90 m/min ili 5,4 km /h.
Međutim brzina kretanja ljudi po horizontalnoj površini u zatvorenim prostorijama gde je prisutan veći broj ljudi je znatno manja. Prema NFPA 101 standardu ona iznosi:
  prosečna brzina kretanja zdravih osoba po horizontalnoj površini iznosi Vh = 1,2 m/s ili 72 m/min, ali kod gužve ili panike kakva se javlja pri evakuaciji ova brzina može da se smanji na 0,75 m/s ili 45 m/min.
  prosečna brzina kretanja zdravih osoba niz stepenice iznosi Vns = 10 m/min,
  prosečna brzina kretanja zdravih osoba uz stepenice iznosi Vus = 8 m/min.
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 5: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Širina izlaznih puteva utvrđena je prema broju osoba koje se evakuišu, i to: prema fizičkom stanju osobe (zdrava, povređena, invalidna osoba) i odeći koju nose (zimska, letnja). Tako:
  zdravoj osobi treba širina izlaza od minimalno 560 mm,
  osobi u invalidskim kolicima 680 mm, i
  osobi sa štakama 840 mm.
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 6: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Minimalne dimenzije vrata za evakuaciju date su tabelom 2:
Broj osoba u prostoriji | 1 | 2 | 2 - 10 | 10 - 50 | 50 - 100 | > 100
Minimalna širina vrata m | 0,62 | 0,72 | 0,92 | 1 | Dvokrilna ili dvoje dovoljno razdvojenih vrata | Više dvokrilnih i/ili jednokrilnih vrata
Visina vrata m | 2,05 | 2,05 | 2,05 | 2,05 | 2,05 | 2,05
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 7: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Kod proračuna potrebnog vremena za evakuaciju iz jednog objekta potrebno je uzeti u obzir dva bitna faktora koji utiču na određivanje potrebnog vremena evakuacije, a to su:
  vreme potrebno za napuštanje pojedine prostorije i
  vreme potrebno da se napusti ugroženi objekt.
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 8: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Vreme potrebno za evakuaciju iz prostorije
Kod proračuna potrebnog vremena za evakuaciju iz prostorije potrebno je izračunati vreme za koje može osoba iz najudaljenijeg mesta u prostoriji da napusti prostor i vreme koje je potrebno da sve osobe koje se nalaze u prostoriji napuste prostoriju.
Proračun vremena za najduži put iz prostorije izračunava se prema sledećoj formuli:
Proračun vremena potrebnog da sve osobe napuste prostoriju izračunava se prema:
Smax m - maksimalna dužina puta i
Vh m/min - brzina kretanja osoba po horizontalnoj površini
N - broj osoba u jednoj prostoriji, pri čemu se kao osnovica za proračun uzima 1 osoba po m2 neto prostorije, ako se nezna tačan broj osoba
d - ukupna širina svih vrata
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 9: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Vreme potrebno za evakuaciju iz prostorije
Ukupno vreme evakuacije računa se prema formuli:
Posle određivanja vremena evakuacije tu, tp i tv iz jedne prostorije, maksimalno vreme evakuacije zapravo predstavlja ukupno vreme evakuacije, dakle:
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 10: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Vreme potrebno za evakuaciju iz objekta
Vreme potrebno za evakuaciju prema maksimalnoj dužini puta:
Kod izračunavanja vremena potrebnog za savladavanje najdužeg puta do izlaza iz objekta tpmax potrebno je uzeti u obzir sve vrste kretanja:
tmax (min) - maksimalno vreme potrebno za napuštanje jedne prostorije,
tpmax(min) - vreme potrebno za savladavanje najdužeg puta.
S1 m - maksimalna dužina puta po horizontalnoj površini,
S2 m - maksimalna dužina puta niz stepenice,
S3 m - maksimalna dužina puta uz stepenice.
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 11: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Vreme potrebno za evakuaciju iz objekta
Kod određivanja dužine puta evakuacije preko stepenica uzimaju se najčešći tipovi stepeništa:
  Jednokrako stepenište bez međupodesta
  Dvokrako stepenište s međupodestom
  Jednokrako stepenište s međupodestom
h m – visina stepeništa
b m – širina stepeništa i
n – broj spratova
h m – visina dvokrakog stepeništa
b m – širina stepeništa i
n – broj spratova
h m – visina stepeništa
b m – širina stepeništa i
n – broj spratova
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 12: Izračunavanje potrebnog vremena za evakuaciju iz objekata
Vreme potrebno za evakuaciju iz objekta
Izračunavanje potrebnog vremena za evakuaciju iz objekta prema propusnoj moći izlaznih vrata:
tmin (min) – ukupna vremena evakuacije iz svake prostorije,
N = ukupan broj osoba koji izlaze iz objekta,
d - ukupna širina svih vrata
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.

## Slide 13: Izrada plana evakuacije i spasavanja
Grafički deo je sastavni deo plana. Grafički prikaz objekta po pojedinim evakuacionim zonama potrebno je vidljivo istaknuti u svakom delu prostora iz kog se izvodi evakuacija, odnosno u svakoj evakuacionoj zoni na lako uočljiva mesta. Ta mesta mogu biti ucrtana na samim nacrtima. Time je ispunjena obveza prema kojoj radnici mora da se upoznaju s planom evakuacije i spasavanja.
Grafički deo plana evakuacije
Notes: How presentation will benefit audience: Adult learners are more interested in a subject if they know how or why it is important to them.
Presenter’s level of expertise in the subject: Briefly state your credentials in this area, or explain why participants should listen to you.